MONITORING AND EMERGENCY

ACTION PLAN

____________________________________

for the

______________ Freshwater Impoundment

ID#_______________

Located at or near

___________, ____________ County, West Virginia

Operated by: (Include contact info)

Prepared by:

NOTE: This example plan is intended to be used as a guide for implementation of monitoring and emergency procedures for centralized pits and impoundments. It is not necessarily all inclusive. Site specific conditions should be reviewed and the plan adapted to reflect local conditions.

TABLE OF CONTENTS*

*Adjust table of contents to plans

Section 									Page Number

INTRODUCTION .................................................................................................................. 3

Location Map ........................................................................................................... 4

Site Plan   ................................................................................................................. 5

PART I- MONITORING PLAN AND INSPECTION SCHEDULE .................................... 6

Section A - Normal Conditions ................................................................................ 6

Section B - Dangerous Conditions .............................................................................7

Section C – Standby Alert …………………………………………………..………8

PART II- EMERGENCY ACTION AND EVACUATION PLAN ...................................... 11

Section A - Notification of Agencies ....................................................................... 12

PART III - POST EVACUATION NOTIFICATION PROCEDURE …………………..…. 13

Section A -Should No Failure Occur ........................................................................ 13

Section B - Should Failure Occur ............................................................................. 13

PART IV -ADMINISTRATIVE AND RECORD ………………………………………….…14

Section A - Signature and Distribution list ................................................................. 14

Section B -Inspection Record ..................................................................................... 15

APPENDIX A – HAZARD EVALUATION AND BREACH CALCULATIONS ...................16

# INTRODUCTION

Purpose of Plan:

The purpose of this document is to provide for monitoring of the ABC Freshwater Impoundment under various conditions so that an emergency situation at the impoundment will be observed promptly and reported to agencies and persons who may be affected. This document also provides a plan for the orderly notification and evacuation of downstream residents to a place of safety in the event of a potential or actual impoundment failure.

Brief Overview of Impoundment:

The ABC Freshwater Impoundment is an earthen structure with a maximum exterior berm height of XX.X feet and impounds a maximum water volume of XX.X acre-feet. It was designed by a WV registered professional engineer and it’s construction will be certified by the engineer to have been constructed according to design prior to filling. The impoundment will be constructed with an impervious 60 mil. geo-membrane liner to ensure it is independent of both surface and subsurface water sources. The impoundment will be filled using a waterline pumping fresh water from the West Virginia River. The inflow and outflow of water will be controlled by portable pumps to maintain a normal freeboard of 2 feet.

Impoundment Location:

The ABC Freshwater Impoundment is located just south of US Route 66 approximately 1.2 miles west of Smalltown, WV. The impoundment is approximately 0.5 miles from US Route 66 on a private access road which crosses little Salt Lick Creek.

How to Use This Document:

Persons using this plan will find a sequence of actions to be taken depending on rainfall and site conditions. A summary of where to find specific monitoring, reporting, and evacuation requirements can be found on the Table of Contents (See Previous Page).

## Location Map

______________ Freshwater Impoundment

______________ County, WV

Road Map

Topo Map

## Site Plan

# PART 1- MONITORING PLAN AND INSPECTION SCHEDULE

## Section A - Normal Conditions:

Inspection Frequency shall follow requirements of W. Va Code §35-4-21 and consist of inspections at a minimum of one every two weeks under normal weather conditions.

| Action | Responsibility |  |
| --- | --- | --- |
| - Inspect weekly/bimonthly/monthly as appropriate to the condition of the impoundment. If a serious problem is found proceed immediately to Section B or C as appropriate. Inspections shall include the following: | Primary Person | Alternate Person |
|  | John Doe (304) 555-1212 | Jane Doe (304) 555-1213 |
| - Inspect the condition of the exposed / visible geo-membrane liner for deterioration and potential weakening. |  |  |
| - Verify the water level is consistent with the scheduled input and withdrawal of water. |  |  |
| - Verify embankments show no signs of movement or instability. |  |  |
| - Remove debris (tree branches, leaves, trash, etc.) from the impoundment area. |  |  |
| - Verify the integrity of the security fence and gate. |  |  |
| - Inspect the inflow and outflow pumping systems for degradation to the geomembrane liner and / or berm. |  |  |
| - Look for signs of erosion along the entire face of the berm. |  |  |
| - Check for potential seeps or piping through the berm. |  |  |
| - Other: include any site specific inspection criteria. |  |  |

## Section B - Dangerous Conditions:

The following monitoring and inspection schedule will be used for heavy or extended rainfall, flash flood warnings, earthquake, snow-melt, or serious new problems found under normal conditions such as slips, sinkholes, or piping. Inspection will occur within 24 hours of a heavy rain event, defined as two (2) inches of rain or more in a six (6) hour period.   If a problem is observed which could lead to failure, proceed immediately to Section C.

Occurrence of an earthquake of sufficient magnitude to cause structural damage to buildings or

property in the general area of the impoundment shall be considered an "adverse condition". Damage from an earthquake may be internal to the impoundment and problems may not appear for days or weeks after the event. The impoundment shall be inspected immediately after the quake and daily for several weeks thereafter. Attention should be directed to looking for cracks, slips, new wet or seepage areas and leakage, both on the face of the berm and in the natural ground areas downstream.

If possible, the impoundment water level shall be decreased prior to forecast extended rainfall or immediately after concerns are observed.

| Action | Responsibility |  |
| --- | --- | --- |
| - Adverse conditions inspections shall be performed daily or more often as necessary and shall include the following: | Primary Person | Alternate Person |
|  | John Doe (304) 555-1212 | Jane Doe (304) 555-1213 |
| - Inspect the condition of the exposed / visible geo-membrane liner for deterioration and potential weakening. |  |  |
| - Verify the water level is consistent with the scheduled input and withdrawal of water. |  |  |
| - Verify embankments show no signs of movement or instability. |  |  |
| - Remove debris (tree branches, leaves, trash, etc.) from the impoundment area. |  |  |
| - Verify the integrity of the security fence and gate. |  |  |
| - Inspect the integrity of surface berms and surface runoff water to ensure no uncontrolled or excessive erosion. |  |  |
| - Inspect surface berms and up gradient drainage, ensure no surface water flow into impoundment. |  |  |
| - Inspect the inflow and outflow pumping systems for degradation to the geomembrane liner and / or berm. |  |  |
| - Look for signs of erosion along the entire face of the berm. |  |  |
| - Check for potential seeps or piping through the berm. |  |  |
| - If problem is observed which could lead to failure, proceed immediately to Section C |  |  |

## Section C - Standby Alert:

The following procedure will be used when the condition of impoundment has deteriorated and has been determined to be threatening to the integrity of structure, or the water surface rises to the predetermined critical level of 1 foot above freeboard elevations.

If possible, the impoundment water level shall be decreased as soon as possible after standby alert concerns are observed. The impoundment shall be drawn down to freeboard elevations.

| Action | Responsibility |  |
| --- | --- | --- |
| - Constant surveillance; decrease impoundment or pit volume, if possible. | Primary Person | Alternate Person |
|  | John Doe (304) 555-1212 | Jane Doe (304) 555-1213 |
| - Monitor the surface elevation of the water and the 2 foot of freeboard. |  |  |
| - Inspect the condition of the exposed / visible geo-membrane liner for deterioration and potential weakening |  |  |
| - Look for signs of erosion along the entire face of the berm. |  |  |
| - Inspect the inflow and outflow pumping systems for degradation to the geomembrane liner and / or berm. |  |  |
| - Check for potential seeps or piping through the berm. |  |  |
| - Alert potential affect parties of the danger. |  |  |

Notify agencies according to checklist in the following tables

| AGENCIES TO BE NOTIFIED |  |  |  |  |
| --- | --- | --- | --- | --- |
| Check When Completed |  |  |  | Phone |
|  |  |  | Local 911 | 911 |
|  |  |  | WVDEP Office of Oil and Gas |  |
|  |  |  | Local Oil and Gas Inspector |  |
|  |  |  | Spill Reporting Number (if waste pit release) |  |

| AGENCY NOTIFICATION CHECKLIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Check When Completed |  |  |  |  |
|  |  |  | Identify yourself |  |
|  |  |  | Refer to the Impoundment as (Name of impoundment or pit) at (Name of town / community). |  |
|  |  |  | State WVDEP Oil and Gas Impoundment ID #. |  |
|  |  |  | Advise the person that you are calling as required by the emergency action plan. |  |
|  |  |  | Stat the condition of the impoundment. |  |
|  |  |  | State that a standby alert has been declared. |  |
|  |  |  | Advise the person contacted of any requested assistance or action. |  |
|  |  |  | Describe the conditions that warranted the standby alert. |  |
|  |  |  | Describe the immediate danger and risks to surrounding people and property. |  |
|  |  |  | Describe the immediate actions being conducted to avert further danger. |  |
|  |  |  | Answer any questions. |  |
|  |  |  | Document the time and with whom you speak at the notified agencies (Name / title) |  |

If failure of the structure is deemed to be imminent, immediately begin notification and evaluation procedures, as described in Part II, Emergency and Evacuation Plan

# PART II- EMERGENCY ACTION AND EVACUATION PLAN

Begin emergency evacuation if failure of pit or impoundment is eminent.

Section A - Notification of Agencies:

Notify the following agencies of an evacuation notice if not already on-site.

| AGENCIES TO BE NOTIFIED |  |  |  |  |
| --- | --- | --- | --- | --- |
| Check When Completed |  |  |  | Phone |
|  |  |  | Local 911 | 911 |
|  |  |  | WVDEP Office of Oil and Gas |  |
|  |  |  | Local Oil and Gas Inspector |  |
|  |  |  | Spill Reporting Number (if waste pit release) |  |

Section B – Emergency Evacuation

Working with emergency response personnel and any available company representatives, begin emergency notification of potentially affected surrounding people, residences and businesses, with the objective of moving all people out of harm’s way.

Based on Hazard Evaluation and survey, contact the people and organizations on downstream of impoundment that may be impacted by a failure. Inform them of the potential for impending danger and assist them with evacuation to a safe location, if needed.

# PART III- POST EVACAUATION/ROAD CLOSURE PLAN

Section A - Should No Failure Occur:

1. Notify agencies according on checklist below to cancel evacuation order (if not already onsite).

| AGENCIES TO BE NOTIFIED |  |  |  |  |
| --- | --- | --- | --- | --- |
| Check When Completed |  |  |  | Phone |
|  |  |  | Local 911 | 911 |
|  |  |  | WVDEP Office of Oil and Gas |  |
|  |  |  | Local Oil and Gas Inspector |  |
|  |  |  | Spill Reporting Number (if waste pit release) |  |

- Inform affected parties that the emergency has past and it is safe to return.

- Immediately begin any efforts to stabilize the structure and/or reduce water volume. An engineering analysis and evaluation will begin to determine root cause of problems and corrective actions.

# PART IV - ADMINISTRATION AND RECORD KEEPING

XXXX Engineering, Inc. will distribute copies of the Monitoring and Emergency Action Plan for the ZZZZ Fresh Water Impoundment on behalf of ABC Operator, LLC., within fifteen days (15)

after receipt of the WVDEP Office of Oil and Gas Approval to the persons named in the distribution list below.

Section A - Distribution:

Names and Addresses of all persons or agencies retaining a copy of this plan:

COMPLETE MAILING ADDRESS

## Hazard Evaluation and Breach Calculations

The purpose of this hazard evaluation is to survey the area surrounding a pit or impoundment site applying for a certificate of approval, and evaluate likely impacts to surrounding area should a failure occur. By determining the potential for hazardous impacts, it is expected that these risks caused by failure may be reduced or eliminated by proper engineering practices. This evaluation will also aid in the planning of, and implementation of, the emergency action plan required by regulation.  Specific details of this evaluation may vary depending on the site conditions, such as; topography, nearest neighbors, surrounding land use, proximity to roads, construction details of pit or impoundment, and distance to any of the above. Evaluation of impacts of catastrophic failure will use any one of a number of accepted engineering models.

The hazard evaluation will consist of these elements:

- Site description (ex. ridge top, side hill, river bottom)

- Pit or Impoundment description, with size, general shape, general construction method, (incised, side hill embankment, etc.)

- Expected, or most likely flow path of liquid and / or solids , should failure occur. It may be necessary to consider more than one possible flow paths.

- Engineering and hydraulic analysis to determine the areal extent of impacts a catastrophic failure will inflict. There are a number of accepted modeling approaches to do impoundment breach calculations that may be applied to get a general prediction of these impacts. One source of information on these models is the U.S. Department of the Interior, Bureau of Reclamation, Dam Safety Office. A brief overview of some models may be found at:   http://www.usbr.gov/pmts/hydraulics_lab/twahl/breach/breach_links.html

- Detailed description, and count, of structures in the expected flow path(s). Structures that will be surveyed will include, but not limited to; homes, businesses, schools, barns, any potentially occupied structure, roads, utilities, mining facilities. In area with coal mining history, review whether site is over active or inactive deep mines, and evaluate subsidence / break-through potential. This survey of surrounding structures will include all structures that are in the predicted impact zones as defined by dam break models or sound engineering/hydraulic evaluation.

- Results of this survey will be used in planning the emergency action plan. Parties that may be affected in an emergency situation will be immediately notified and actions will be taken to protect life and property.  The applicant will maintain contact lists for potentially impacted individuals. Personal information concerning the occupants of dwellings will not be included in public records submitted with this plan but will be maintained by applicant. Emergency response agency contact information will also be maintained.

- Results of the survey will also be used to consider additional engineering controls that will prevent these identified risks.

In situations where the potential for adverse impacts to surrounding community is high, or where there is potential for loss of life, it is expected that alternative sites be chosen for impoundment or pit installation.  The Office of Oil and Gas has the authority to deny any application for certificate of approval which poses excess risk to the community or environment. (W.Va. rule §35-4-21.1)

## Emergency Action Plan Site Map (potential flow paths, neighbors likely impacted, nearest streams, etc.)

Emergency Action Plan: Residence and Neighboring Property Survey:

Using the hazard evaluation, list the nearest neighbors and potentially affected parties.  This list shall not be made public.